#### INSTALLATION and capsule replacement INSTRUCTIONS

For DELTEC

EMP SURGE SUPPRESSORS

### MOUNTING

Using the 7/16 series bulkhead fixing thread and nut, the EMP device may be fixed into a 30.5mm dia hole (with anti-rotation keying) in a grounded plate or bracket up to 16mm think.

##### INSERT - IMAGE

Ensure the gas arrestor sub-screw is on the outside (accessible side) of the metal wall.

Note - the metal wall/bracket/plate must be adequately earthed.

## REPLACING THE GAS ARRESTOR CAPSULE

1. Press a 3/16" AF Allen head key through the grub-screw label into the covered hex hole (rotate the Allen key to, find the correct alignment.

2. Unscrew the grub-screw and remove the old gas tube and wavy-washer.

3. Replace the old O-ring and wavy-washer with the new parts provided in the kit.

4. Fit the new gas tube.

5. Screw the grub-screw in tight (recommended torque is 6.0 Nm)

6. Stick the/a new label over the grub-screw

### AVAILABLE REPLACEMENT KITS

Part number SSC90-KIT 	90V Gas Arrestor

Part number SSC230-KIT 	230V Gas Arrestor

Part number SSC900-KIT 	900V Gas Arrestor

Part number SSC1500-KIT 	1500V Gas Arrestor

Instruction Sheet No.136-372 (revised)

Sunday, Sun, Dec 01, 2002

input.doc