MOUNTING 
The mounting details for the surge suppressor are shown below 

~.- 

30.5 

--.# 

Lf)' t'..: r- 

\~ 

;~i 

j~, 
~ ;-:i 
,0 :' : 
,i ": ,~j' 

. , 

. 

Figure 1. 

Mounting details 

Figure 1 

Ensure the gas arrestor subscrew is on the outside of the metal wall. Note, the metal wall must be earthed. 
~ fl' 
REPLACING THE GAS ARRESTOR "~ ,~ 
1. Press a 3/16" Allen head key through the grubscrew label into the covered hex hole (rotate the Allen key to,ifind the correc~ alignme~~!, . 
-,,--. c-""---~c '"' ,. 
---'~-=--" .=~~- ~. ~ 2. Unscrew the grubscrew and remove the old gas tube. {i:f .'""'-:00-. 
3. Replace the old O-ring and wavy washer with the new parts prov1ded .1n the kit. 

4. 

5. 

6. 

Fit the new gas tube. 

Screw the grubscrew in tight (recommended torque is 6.0 Nm) 

stick the new label over the grubscrew 

AVAILABLE REPLACEMENT KITS 

Part number 

SSC90-KIT 

Part number 

SSC230-KIT 

Part number 

SSC900-KIT 

Part number 

SSC1500-KIT 

~,~ 

90V Gas Arrestor 

230V Gas Arrestor 

900V Gas Arrestor 

1500V Gas Arrestor 

\MK\PROD\ANC\SSC 
Instruction Sheet No.136-372