## Sheet0
S-2500/3000W系列开关电源 S-2500/3000W Series Switch Mode Power Supply
Application & Features | 概述
·低价格、高可靠 ·105℃输出电容器 ·全球适用AC输入电源 ·效率高、工作温度低 ·软启动电流、有效降低AC输入冲击 ·有短路保护、过载保护 ·体积小、重量轻 ·100%满负荷烧机测试 ·内装EMI滤波器、纹波极小 | ·Low price, high reliability ·105℃ output capacitor ·AC input power supply is applicable all over the world ·High efficiency and low operation temperature ·Soft start current, effectively reduce AC input impact ·Short circuit protection. Overload protection ·Small size and light weight ·100% full load burn-in test ·Built-in EMI filter, minimal ripple & noise
性能 型号 Specification Model | S-2500-12 | S-2500-24 | S-2500-36 | S-2500-(0-48) | S-3000-24 | S-3000-48
直流输出电压 DC output voltage | 12V | 24V | 36V | 1-48V | 24V | 48V
输出电压容差 Output voltage tolerance | ±1% | ±1% | ±1% | ±1% | ±1% | ±1%
额定输出电流 Rated output current | 208A | 104A | 69A | 52A恒流 | 125A | 62.5A
输出电流范围 Output current range | 0~208A | 0-104A | 0-69A | 0-52A | 0-125A | 0-62.5A
纹波及噪音(注3) Ripple & noise (Note 3) | 150mVp-p | 150mVp-p | 200mVp-p | 200mVp-p | 240mVp-p | 480mVp-p
进线稳定度(注4) Stability of incoming line (Note 4) | ±0.5% | ±0.5% | ±0.5% | ±0.5% | ±0.5% | ±0.5%
负载稳定度(注5) Load stability (Note:5) | ±0.5% | ±0.5% | ±0.5% | ±0.5% | ±0.5% | ±0.5%
直流输出功率 DC output power | 2500W | 2500W | 2500W | 2500W | 2000W | 48V-2000W
效率 Effciency | 84% | 84% | 85% | 85.5% | 86.5% | 87%
直流电压可调范围 Adjustable range of DC voltage | ±10% | ±10% | ±10% | ±10% | ±10% | 0~48V
输入电压范围 AC Input voltage range | 190-240VAC/47-63Hz
输入电流 Input current | 7A/230V
冲击电流 Surge current | 50A/230V
漏电流 Leak current | <3.5mA/240VAC
过载保护 Over-load protection | 105%-150%类型：切断输出 复位：自动恢复 105%-150%: cut-off with automatic reset/recovery (when overload removed)
过电压保护 Over-voltage protection | 110%-135%VO
高温保护 Over-temperature protection | ≥270℃ 切断输出(0-50V） ≥270℃ over-temperature cut output (0-50V)
温度系数 Temperature coefficient | ±0.03%/C (0-50℃)
启动、上升、保持时间 Set up, rise, hold-time | 1.5s, 50ms, 20ms
抗震性 Resistance to shock | 10-500Hz 2G 10min/1周期，时长60分，各轴 10-500Hz.2G 10min/1cycle for 60 minutes on each axis
耐压性 Resistance to pressure | 输入输出间：1.5KvAC 输入与外壳：1.5KvAC 输出与外壳：0.5KvAC Input/Output: 1.5kVac input and housing: 1.5kVac output and housing: 0.5kVac
隔离电阻 Isolation resistance | 输入输出间：输入与外壳，输出与外壳:500VDC/ 100MΩ Input/output: input to chassis, output to chassis :500VDC/ 100MΩ
工作温度，湿度 Operating temperature, humidity | -10℃~+60℃(参考输出特性图)，20%~90%RH -10℃~+60℃ (Refer to the output characteristics diagram) 20%~90%RH
存储温度、湿度 Storage temperature and humidity | -20℃~+85℃, 10%~95%RH
重量 Weight | 4.2kgs [are they really all the same?]
安全标准 Safety standards | 满足UL1950要求(不申请标记) Meets UL1950 requirement (not yet approved mark)
注：1.以上参数测试条件为：230VAC输入、额定负载、25℃70%Rh、湿度。 2.容差:包括设定容差，线路稳定、负载稳定度(注5)。 3.纹波测试:20MHz用"A12"双绞线，中断用0.1uF&47uF电容器短路。 4.进线电压稳定度测试:满负载时进线最低电压到最高电压。 5.负载稳定度测试:负载从0%到100% Notes: The test conditions for the above parameters are as follows: 1. 230VAC input, rated load, 25 ° C 70%Rh, humidity. 2. Tolerance: including the set tolerance, line stability, load stability (Note 5). 3. Ripple test: 20MHz with "A12" twisted pair wire, interrupt with 0.1uF & 47uF capacitor short circuit. 4. Input voltage stability test: minimum input voltage to maximum input voltage at full load. 5. Load stability test: Load from 0% to 100%